| Avoidance of danger from overhead electric power lines |  |  |
| --- | --- | --- |
| INTRODUCTION 1 Contact with live overhead lines kills people and causes serious injuries every year. A high proportion about one third - of inadvertent line contacts prove fatal. This document sets out procedures which, if adopted, will reduce both the number of these tragedies and the associated costs of repairs and lost production due to interrupted supplies. 2 The advice is aimed at those in control of any kind of work under or near to overhead electric lines. 3 It is particularly relevant to, construction and covers all work where long or high plant or equipment, such as scaffold poles, vehicles, cranes are operated or moved under or near to these lines. The specific requirements for safety of work on or near overhead electric lines should be set out in the applicable Electrical Safety Rules: THE RISK 4 Contact with overhead electric lines can be lethal whether they are carrying a voltage as high as 400 000 V or as low as 230 V. | 5 Overhead lines consist usually of bare (uninsulated) conductors (sometimes called cables) supported via insulators by wooden poles or metal towers and structures. 6 If a crane jib, tipper lorry, excavator, scaffold pole, ladder or similar object makes contact with or approaches near to these lines, an electric current can flow with a risk of fatal or severe shock and burns to any person in the immediate vicinity. 7 This can also occur with objects made from materials such as wood or plastic, which are normally regarded as electrical insulators. If damp or dirty, these may also be capable of transmitting sufficient current to cause dangerous or fatal electric shocks. Note: Actual contact with a power line is not necessary to result in electric shock. A close approach to the line conductors may allow a 'flashover' or arc to take place. The risk of flashover increases as the line voltage increases. |  |

| Avoidance of danger 9 For work at or near overhead power lines, this guide suggests the following actions: a) find out if the work has to be carried out under or near overhead lines (can it be avoided altogether) or, if this cannot be done; (b) divert all overhead lines clear of the work area or, if it is not reasonable for this to be done; (c) make lines dead while the work is in progress or, if this cannot be done; (d) work around the live overhead lines using the precautions outlined in this guidance. In some cases it may be necessary to use suitable combinations of these measures, particularly where overhead lines pass over permanent work areas. | If any such lines are found it should be assumed that they are live unless or until this has been proved otherwise by-their owners. 11 If there are any electric lines over the work area, near the site boundaries, or over access roads to the work area, consult the owners of the lines so that the proposed plan of work can be discussed. Allow sufficient time for the line to be diverted or made dead, or for other precautions to be taken as described below. 12 If the lines can only be made dead for short periods, then the passage of tall plant and, as far as is possible other work around the lines, should be scheduled at these times. 13 Liaison between the persons responsible for the work and the owner(s) of the lines should be continued until the work has been completed. |
| --- | --- |
| Work near overhead lines 10 Pre-planning of safe working procedures is important. The first step in avoiding danger is to find out whether there is any overhead electric line; (a) within or immediately adjoining the work area, or (b) across any route to it. Information may be available from the local electricity supplier about location of their lines. | PRECAUTIONS 14 The precautions depend on the nature of the work at the site. It is strongly recommended they are taken even when work near the line is of short duration. There are three broad categories of this work. (a) Work areas where there will be no scheduled work or passage of plant under the lines. Here barriers can prevent close approach, particularly for construction work (b) Work areas where plant will pass under the lines. Here defined passageways should be made. (c) Work areas where work will be carried out beneath the lines. Here further precautions must be taken in addition to the erection of barriers with passageways. |

Figure 1:	Sites where there will be no work or passage of plant under lines.  Examples of ground level barriers and high bunting.  Similar precautions apply to lines supported on steel towers.

| Work areas where there will be no work or passage of plant under the lines 15 Danger can be reduced by erecting ground level barriers parallel to the overhead line to prevent any part of the mobile plant approaching too close to the line (see Figure 1). The recommended minimum distance from a barrier to the position, projected vertically onto the ground, of the conductor nearest to that barrier is 6 metres. | 20 It is recommended that ground level barriers should be substantial enough that they are not easily moved. Examples are: (a) a stout post and rail fence; or (b) a tension wire fence earthed at both ends, having flags on the wire, the earthing arrangements of the fence being agreed in consultation with the electricity supplier; or |
| --- | --- |
| Note: The owner of the line(s) may advise a minimum distance greater than 6 metres, depending on the voltage of the overhead line. In certain cases, particularly where high voltage lines with long spans are involved, allowance should be made for lateral swing of the conductors, to maintain the safe distance from barriers to the overhead line at all times. | (c) large steel drums, for example 182 litre (40 gallon) oil drums filled with rubble and placed at frequent intervals; or (d) an earth bank not less than 1 metre high and marked by posts to stop vehicles; or (e) substantial timber baulks or concrete blocks to act as wheel stops. |
| 16 Where this minimum distance could be encroached upon by parts of mobile plant (e.g. crane jibs, excavator buckets etc.), it is recommended that the plant operators are given an additional indication of the position of the barriers. A line of coloured plastic flags or 'bunting', mounted at a height of from 3 to 6 metres above ground level immediately over the barriers, could be used. Where bunting etc. is provided at heights of 6 metres, the supports for the bunting should be sited at least 9 metres from the position of the nearest conductor to the barrier when projected vertically onto the ground. Care is necessary when erecting bunting and flags to avoid contact or approach near to the conductors. 17 Where plant such as a mobile crane is used, the recommended minimum horizontal distance of the ground level barriers from the path of the overhead lines is 6 metres plus the length of the crane jib or other overhanging part of the plant. Note: The owner of the line may recommend a greater distance than this if the nature of the line requires it. In such cases the supplementary flags or bunting need not be provided. 18 Measurements should be made horizontally, from underneath the nearest conductor in the line, at ground level only. It is extremely dangerous to attempt to take vertical measurements. 19 Where there will only be access on one side of the line, a barrier on this side only will suffice, but if the overhead line crosses the site, barriers will be required on both sides of it. If there is danger to people carrying metal scaffold poles, ladders or other conducting objects, then the barrier should be so arranged to prevent access by both people and mobile plant. | Fences, posts, oil drums etc. should be made as visible as possible, for example by being painted with red and white stripes. Alternate red and white plastic warning flags may be hung on or immediately above any fence line to improve their visibility. 21 It is strongly recommended that the storage of materials in the area between the overhead line(s) and any ground level barrier is prohibited. Work areas where plant will pass under lines 22 Where passage is required under the overhead line either along an access road or from one part of the work area to another, it is recommended that the danger area should be made as small as possible. This should be achieved by restricting the width of the passageway to the minimum needed for the safe crossing of plant. It is safest if the passageway crosses the route of the line at right angles (see Figure 2). The following precautions are recommended: (a) The number of such passageways should be kept to a minimum. (b) The passageway should be fenced to define its route, and goal posts erected at each end to act as gateways in the barriers running parallel to the overhead line. (c) The goal posts should be constructed from rigid, non-conducting material such as suitable timber or plastic pipe and distinctively marked in, for example, red and white stripes. (d) At either side of the passageway, on or near the goal posts, there should be warning notices giving the cross-bar clearance height and instructing drivers to lower jibs, tipper bodies etc. and keep below this height while crossing. (e) On sites where work continues after dark the notices and cross-bars should be lit. It has also been found that illuminating the conductors is useful. The light fittings used for this illumination should be sited at ground level projecting the light upwards towards the conductors. |

| (f) Additional warning notices should be erected on the approaches to the crossing, say about 30 metres away. (g) The surface of the passage way should be levelled, firmed up and well maintained to prevent undue tilting or bouncing of the equipment when under the overhead line. 23 Carefully consider the speed and stopping distance of the vehicles and plant when determining the layout and location of goal posts and warning signs. This will assist in positioning the goal posts sufficiently far from the overhead line(s) to prevent any vehicle or plant coming to rest beneath the line(s), if the goal posts are struck. 24 In situations where passage under the line cannot be confined to a single track (e.g. road construction), it may not be possible to restrict the passageway to a width which can be spanned by a rigid non-conducting goal post. In these cases, tensioned steel ropes or plastic ropes may have to be used (see Figure 3). It is recommended that such ropes are sited on both sides of the line at least 12 metres horizontally from the path of the outer conductor. This increased distance is essential to reduce danger from loss of safety clearance due to the possibility of ropes being stretched by cranes and other appliances moving towards the line. Where steel ropes are used, they should be effectively connected to earth at each end. Coloured 'bunting' can be attached to the tensioned rope to make it more easily visible. Work areas where work will be done beneath the line. 25 If work beneath live overhead lines cannot be avoided, barriers, goal posts and warning notices should be provided. However, they will not prevent danger from upward movements of cranes, excavators or other appliances, nor will they prevent direct contact by workers where buildings or structures are being erected beneath the lines. Work at ground level only (e.g. pipe laying) 26 The following precautions are recommended: (a) The safe clearance required beneath the overhead lines should be ascertained from the owner of the line(s). (b) Plant, equipment or hand tools that could reach beyond the safe clearance limit should not be taken under the line. (c) Plant such as cranes and excavators should be modified by the addition of suitable physical restraints so that it cannot reach beyond the safe clearance limit. Restraining devices may be fitted to the derricking or slewing mechanism, or both, as required. They may take the form of mechanical stops, or of limit switches for electrically driven cranes, or oil or fuel valves respectively for engine driven cranes with hydraulic or mechanical transmission. (d) Cranes with telescopic or fly jibs may need additional restraining devices to prevent alteration in length of jib or angle of fly jib. | (e) Access for plant and materials and the working of plant should be under the direct supervision of a suitable person appointed to ensure that safety precautions are observed. Erection of buildings or structures underneath an overhead line 27 In cases where buildings or structures are to be erected under overhead lines (and for those occasions when work has to be done at or from an existing building) increased risks will arise because of the chance of safe clearances being reduced by the proximity of the works and by provision of the required access above ground level. 28 If the lines cannot be diverted or made dead as described in paragraphs 9 to 12, the following precautions are strongly recommended: (a) The owner(s) of the line(s) should be consulted about proposed working methods. (b) The work should be carried out under the direct supervision of a suitable person, familiar with the risk, and appointed for the purpose of ensuring that safety precautions are observed. (c) The use of tools or items of equipment, e.g. scaffold poles, ladders etc., which can reach high enough to touch the overhead line (or going close enough to it to cause a flashover to take place), should be avoided. (d) A horizontal barrier of timber or other insulating material should be erected beneath the live conductors to form a roof over the construction area. Alternatively, in some cases, an earthed steel net may be used. In either case this work should be carried out only after agreement with the owner(s) of the line(s) and it may be necessary to enable safe erection or dismantling of the barrier to have the line(s) temporarily made dead. Use of insulating guards and proximity devices 29 The use of insulating guards to protect conductors from being contacted by jibs, scaffold poles, tipper lorries etc. and/or proximity warning devices without other safety precautions are not accepted. |
| --- | --- |

Figure 2:	Sites where plant will pass under the line.  Example of rigid goal posts and barriers.  Similar precautions apply to lines supported on steel towers.

Figure 3:	Sites where plant will pass under the line.  Example of the use of tension ropes across wide access points.  Similar precautions apply to lines supported on steel towers.

| Planning and Training 32 Where work in open areas or fields is taking place it is impractical to erect barriers and goal posts around the overhead lines. Such devices are more appropriate for use at gateways, on tracks and at access points. For open area work the following measures are recommended: Planning 33 Identify all overhead lines crossings present on the land in question and mark them on a suitable plan. This should be kept available at all times. 34 Check with the owner(s) of the line(s) what the maximum safe working height is for any sections that tall equipment may approach. 35 Find out the maximum height and vertical reach of plant and machinery. Remember to take into account any aerials or other similar projections beyond the designed working height of the plant and machinery. Training 36 Everybody who works near overhead lines with a machine or equipment needs to know what the dangers are and the precautions to take. Visitors (including contractors) 37 Instruct contractors about the presence and dangers of the overhead lines. Make sure they know where the lines are and tell them the precautions they need to take. Routes can be marked with safety signs to warn all visitors of the dangers. | Use of machinery 38 The following activities should not be carried out within 9 metres horizontal distance of overhead power lines supported on wooden poles and 15 metres for those supported on metal towers and structures: (a) tipping trailers or lorries, (d) operating materials handlers; (e) working on top of high machinery. 39 Risks can be reduced by; (a) establishing loading and unloading areas away from overhead lines so that there is less chance of contact; (b) not storing long objects such as pipes or ladders near or under overhead lines; (c) carrying long objects horizontally using two people; 40 Where overhead lines cross normal work activity areas and access routes, diversion of the overhead lines is to be preferred. Where this is not possible, consider creating alternative access points or routes. If this cannot be done, provide suitable warning signs and goal posts and barriers. |
| --- | --- |
|  | Electrical Safety Rules should require that: "All work activity, including...... work near an Overhead Line system, shall be carried out in such a manner as not to give rise, so far as is reasonably practicable, to danger". "No person shall be engaged in any work activity on or so near any live conductor (other than one suitably covered with insulating material so as to prevent danger) that danger may arise unless (a) it is unreasonable in all the circumstances for it to be dead and (b) it is reasonable in all the circumstances for him to be at work on or near it while it is live and (c) suitable precautions (including where necessary the provision of suitable protective equipment) are taken to prevent injury". |
|  | Reference: U.K. HSE doc Guidance Note GS 6 1997 |