|  | # Fire Incident in Condensate Export Pump at Cawthorne Channel Gas Plant |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | ## SPDC/ALFI/2008/05/02 | ##### Exploration and Production (SPDC) |  | # Fountain #145769 | ## Issue Date: May 2008 |  |
| Purpose To focus attention on potential impacts of deviations from manufacturers’ design specifications. Target audience All Facts At about 22:45hrs on 8th November 2007, Cawthorne Channel Gas Plant shut down on ESD due to flame detection on sensors CC74-XZA-328 & CC74-XZA-329. The field operator on duty observed incipient-stage fire on the condensate export pump (P4303A) skid. Nearest fire extinguisher was used to extinguish the fire and situation brought under control. The plant was restarted at 11:40hrs on 9th November 2007. There was damage to the pump and no injury to personnel. Key findings during investigation include the following: - The fire incident occurred on a reciprocating triplex plunger pump (P4303A), used for condensate export service. - The pump, as designed, is always started under load, contrary to manufacturer specification. No bypass line (for start-up) is in place due to design oversight. - The connecting rod and bolts of the pump’s outboard plunger sheared and broke-off from the crankshaft due to fatigue. - Pumping operation continued for 20 minutes after the outboard plunger broke-off. - The shearing-off of the pump connecting rod caused misalignment of plunger strokes, ineffective plunger system lubrication, and increased friction due to rubbing of metal surfaces, heat build-up and ignition. - The CCGP fire detection system operated as designed and the field operator extinguished the fire using nearest available extinguisher. - CCGP operators and attendants have had fire-fighting training. - The field operator was not within the vicinity of the pump export skid during the incident, and there was heavy rainfall/thunderstorm. - The pump’s maintenance plan / MJR is NOT in SAP; consequently no (manufacturer recommended) PM is being done. - There was a conscious decision by Major Projects & Asset team leadership to continue operating CCGP (post-June 2006 militant attack), whilst outstanding design, commissioning and handover issues are being tackled. Learning Points: - Need for Project, Maintenance and OR&A teams to adhere to manufacturers’ recommendation on equipment design, installation and maintenance. - Need for all Cat 0 & 1 equipment to be fully captured in SAP-PM, with approved MJRs and Maintenance plan in place prior to handover/continuous operations. - Need for conducting periodic integrity/reliability checks to assure proper functioning of equipment and HSE gadgets - Need for fire-fighting training to be conducted for all frontline operations staff and station attendants. For More information Contact: akuro.adoki@shell.com |  |  | Condensate Export Pump Skid Scoured Plunger surface Broken & Sheared-off Parts Recommended Actions: - Implement manufacturer’s recommendation on pump installation. Action Party: Ajayi R, (TPE) ECD: 30/9/2008. - Complete ongoing CCIP CMMS activities and update SAP. Action Party: Joel, O. (PECR) ECD: 31/7/2008 - Review CCIP Project recompletion team workscope for completeness (e.g. pumps drain connections, DCS historian, etc). Action Party: Joel, O (PECR) 31/7/2008. - Provide alternative means/flexibility for evacuating CCGP condensate to flowstation. Action Party: Oputa, B (TEEM) ECD: 31/12/2008 |  |  |  |